## Application Process
Topic: Pre-Application/Application Process
Design Challenge: How can we reduce the number of speculative and infeasible applications, while increasing applications of potentially viable projects submitting “complete” applications
that mimimize inefficient back-and-forth between utility and applicant?
Design Components | Status Quo | Option A | Option B | Option C | Option D | Option E | Option F | Option G | Option H | Option I | Option J | Option K
Pre-Application Education | Optional Monthly Interconnection Workshops | Require Interconnection Workshops | Offer more in-depth technical workshops | Provide detailed Checklist for application, and clear standards for interconnection | Rquire certification of Submiting Entity (Installers, Consulting Engineers, or Developer) (at least must attend workshop) | Offer Online Training and Question Module (including interconnection tariff)--Could Use for Certification | Publicize typical interconnection costs for common configurations, and use case studies | Obmbudsperson/administrator/clearinghouse could have role | Change workshop to training w/ or w/o certification
Pre-Application Feasability Check | Utilities Have Pre-Application Discussion at Applicant's Option--Tariff required this option | Provide and regularly update map of DG by each town/substation/ and/or circuit | Provide more detailed map show where at/or approaching saturation, and possibly where DG would be most desireable | Enhance monthly utility reporting to DOER by project to include feeder/circuit location | Log in w address and get information about where considering (circuit), know saturation in that area | Delineate what utility needs to know from developer in pre-application mtg. (size, location) | Standardize information utility can provide in pre-application process(e.g., ratio and stiffness test) | Require Pre-Application Meeting to Discuss Feasability | Add option for written report to DG Provider from utility about proposed DG at their location a la CA Settlement (instead of mtg.) for a fee (e.g. CA $300) | Allow for pre-application email querry--standardize timeframe and what can be given. | MA PE Electrical stamp requirement | When DG reaches certain saturation on circuit, utility would report on it and put in necessary metering
Application Mechanism | NSTAR online for simplified (simple pdf of form), rest via email or snail mail | Online applications should automatically check for application completeness (and not accept application until complete) | Offer Optional On-Line Applications for all | Require On-Line Applications for Simplified Only | Require On-Line Applications for All | Consider centralized statewide application--possibly using project mgt software external to utility IT (tie into utility systems later) | Use online application to track projects throughout the process, and link to other utility systems | Make application more user-friendly and less confusing and consistent (applicants still getting confused) | Incorporate application filling out into training | Add additional information instructions (a la IRS)
Application Fees | None Simplified, Sliding Expedited & Standard | Cover upfront and variable costs if go to online (uniform) sophisticated application process | Add Application Fees for Simplified | Allow Additional Fees for accelerated treatment | Allow Additional fees for other additional services--e.g., pre-application meeting, pre-application report
Other |  | Allow for accelerated treatment in certain circumstances (e.g., project has site control, permits, and financing) | ADR process for application
Provide and regularly update map of DG by each town/substation/ and/or circuit

## Stale Project Mgt
Topic: Stale Project Management
Design Challenge: Can we come up with an enhanced set of protocols and standards at the various stages of the interconnection processes,
review and construction that the utilities can use to clear the process of "stale" projects?
Design Components | Status Quo | Option A | Option B | Option C | Option D | Option E | Option F | Option G | Option H | Option I | Hybrid Option
Overall Stale Project Mgt. Process | Customer "may" be removed from process if don't provide information by certain date--within 15 days or half time utilty has for step (See Tariff 3.4) | Action needs to be non-discretionary and clear when applicant will be removed | Consider subordinating or moving back in queue if don't meet deadlines, rather than removal | Require the applicants to respond at least w/status update within timeframes, even if don't have info requested | Change applicant timeframes in 3.4 to longer timeframes, but make removal non-discretionary | Change "may" terminate to "will" terminate in 3.4 | Rquire applicant at various stages to take next step or withdraw | Consider different removal requirements where there's a queue and not a queue | Allow or require applicant to put up $ to hold place in queue | Meet timeframe plus any extension or have to reapply | Change "may" to "will" but can ask for extension within timeframe, but can't be more than X (consider subordinate in queue--standby--rather than complete removal?)
Application Phase | Clock starts when application submitted, get place in line on a particular feeder/circuit once application is complete (some variability x companies) | Could potentially be resolved if move to required on-line application process | Utility not obigated to reach out to applicant about missing info. more than once
Initial/Supplemental Review |  | For Expedited--Limited to 10 hours of enginneering and fees based on this, but a lot of admin time
Impact Study Phase | Greater of 15 days or half-time utilty has for step
Impact Study Agreement Phase | Greater of 15 days or half-time utilty has for step | Usually more back-and-forth between utility and developer before/during impact (then during the detailed study)
Detailed Study Phase | Greater of 15 days or half-time utilty has for step
Detailed Study Agreement Phase | Greater of 15 days or half-time utilty has for step
Interconnection Agreement | Utility has 10 days for Expedited and 15 Days Standard | Consider shortening timeframe | Add timeline for Customer signing agreement (not in tariff now) e.g., 90 days) | Deposit upfront at application
Construction Phase | 12 months after agreement signing
Other | Some companies "bug" applicants periodically others only when prompted by other applicants in queue | May want to remove projects faster if holding up projects in the queue, alternatively if not holding up others may not rush to remove
Cross-Cutting Issues |  | Consider granularity on timeframes for removal based on size/technology | Consider longer timelines for public entities | Add extension clause process to tariff

## Standard Large Projects
Topic: Standard Track and Large Projects
Design Challenge: Do we need to revise the timelines, screens and procedures, and/or costs embedded in the Standard Track?
Can we continue to accommodate very large projects (e.g., over 1 MW, or project with substantial export) in the Standard Track or do we need a new and separate track?
What would it take to meet timelines in Standard Process for very large projects?
Design Components | Status Quo | Option A | Option B | Option C | Option D | Option E | Option F | Option G | Option H
Dealing With Very Large Projects | Now Thru Standard Process | Massage Standard Process (e.g., change timeframes) | Have new 4th track (or subtrack within Standard) w more review time esp. for Detailed Study (e.g., for over 1 MW w/all "export" or require new circuit) | Inrease staff and other resources , and/or make other process improvements to meet timelines | Temporarily increased timelines until new staff on-board and trained
Screening Process | Supposed to be 15 days, but often taking much longer for larger projects
Impact Study/Detailed Study Timelines | Impact 55 days; Detailed 30 days (but larger projects often require more time for detailed than impact) | Increase staffing & contracting to meet current timelines | Lengthen timelines for all Standard track applicants | Have different timelines for different system requirements/situations | Add 4th track with longer timeframes for very large projects | Add an exceptions process that lengthens timelines for severe weather, certain engineering requirements, volume | Let timelines change depending on volume (e.g., Disney World) | Allow unit cost studies to reduce timeframes (currently used for impact study) | Letter to DPU/Applicant when timeline missed w/rationale
Constructuion timeframes (utility and customer obligations) | Currently in interconnection agreement (not always in there) | Guidelines by size, technology, and configruration
Cost Risk | Utility held to +/- 25% of Impact study and +/- 10% for Detailed Study cost estimates | Option for applicant to forgo Detailed Study and live w/+/- 25% (possibly move faster to agreement and equipment ordering) | Change numbers to something between 25% and 10% | Option for applicant to accept +/- 50% or even actual cost for quicker timeline | Initiate a statewide clearinghouse for equipment perhaps using ACP funds to speed things up
Initial Screen Between Expedited and Standard
Separate Track for Large Projects | Now Thru Standard Process
A) Size |  | > 1 MW | >2MW | >5 or 6 MW (or anything else causes transmission impact)--needs to go thru ISO NE transmission process after distribution process, can stop clock (or use separate process). NSTAR going w/ over 1 MW. Clarify w/ISO | How handle FERC juridisdictional installations and interface with state processes including cost allocation? | Under certain circumstances detailed study can happen in parallel to ISO review
B) Screens
C) Timeframes
D) Engineering/Requirements
E) Fees

## Multiple Projects
Topic: Multiple Projects on a Single Feeder
Design Challenge: Can we come up with an enhanced process for dealing with multiple projects on a single feeder (both multiple applications that need
to be acted on, and multiple installations and upgrades over time)?
Should there be the option (or requirement) to cost share in both study costs and required system upgrades?
Design Components | Status Quo | Option A | Option B | Option C | Option D | Option E | Option F | Option G
Queue Placement | First Come First Served | Give all projects within certain time window on a particular feeder same status | Give higher priority to more feasible projects--site control, permitting, financing (how to police?) | Based on willingness to make security payments, and/or penalties later
Study Costs | Study Each Applicant Sequentially; 2nd, 3rd wait for proceeding studies; if #1 drops out need to relook at study | Keep window open for 3-6 months, and do cluster study w/shared costs (note: need to minimize speculative projects) | Allow opt in to cluster study | Allow opt out of cluster study | Allocate cost by size, or equal costs to each in cluster | Flat fee per MW for study, and update/reconcile periodically (e.g., RI) | Have 3rd party option to review cost estimates, and propose alternatives | Need to define what situations and configurations are eligible for cluster upgrades
Distribution Upgrade Costs | DG Provider Needs System Upgrade Covers Entire Cost | Use similar 5 year rolling cost allocation/reimbursement as for new lines, first one pays entire cost and then reimbursed as additional come on | Have cluster share costs by size or equal costs to each in cluster | Let first few that wouldn't have caused system upgrades in free, and remaining in cluster can share | Let developers self-organize to share upgrade costs | Consider allocating partial upgrade costs to ratepayers that have benefits not just to DG Providers
Other?
|  | Clarify in tariff that if customer ahead in queue leaves, utility needs to reassess subsequent studies and isn't held to original +/- 25% or 10% | SCE/PG&E has put out circuit level clustering proposals--Review | Need to have clear cancellation/stale project policies for both study and upgrade costs

## Track Segmentation
Topic: Track Segmentation
Design Challenge: Should any of the screens that determine whether an applicant go thru the Simplified, Expedited, or Standard tracks be altered in light of
experience, technology improvements, etc. (e.g., the 7.5% of circuit annual peak load, and various size screens)?
Design Components | Status Quo | Option A | Option B | Option C | Option D | Option E | Option F
Simplified Track | <=10 kw single phase, <=25 kw 3-phase inverter-based, <7.5% of circuit annual peak load | Raise 7.5% circuit annual peak load threshold | Change from circuit to line section test--at least to first recloser (potentially with 15% threshold)--may need to increase timelineif info. not readily available | Raise size screen thresholds (above 10 and 25 kw) | Should we consider letting more projects thru simplified but collecting fee (sliding scale/flat) and maybe allowing a bit more time? | Can go to larger size if no exports, while smaller systems that predominantly export may need to go thru expedited | Look at basing on 100% of minimum annual daytime load at customer premise (for solar), otherwise 15%...
Expedited Track | Not Simplified or Standard | Allow larger systems to move thru Expedited | Add size (e.g., 500 kw)/inverter/export thresholds between expedited and standard | Look at CA two-track system, and other leading states | Review screens 6-10
Standard Track | Customer opts for it, or Supplemental Review doesn't determine requirements, utility needs to do study (or certain constellations of multiple inverters)
| If go to Expedited and get kicked to Standard, takes more time than if just went to Standard | Pre-Sceen to give applicants feedback on whether they should be in Standard or Expedited
Simplified Spot Network | Point of coupling on radial distribution system