### Proposed Changes to the Uniform Standards for Interconnecting Distributed Generation in Massachusetts

##### Submitted to:

##### Massachusetts Department of Public Utilities in Compliance with DPU Order 11-75

by the

Massachusetts Distributed Generation Interconnection Working Group

##### September 11, 2012

DRAFT

Table of Contents

Cover Letter from Facilitator

Section 1: Introduction, Background, and Overview	3

Section 2: Application Review Process: Tracks and Revised Screens	 8

Section 3: Application and Construction Timeline	15

Section 4: Adherence to Utility and Applicant Timelines	20

Section 5: Fees	24

Section 6: Pre-Application Report Requirements	26

Section 7: Information Tracking and Reporting	28

Section 8: Other Technical Issues (including Upgrade Criteria and Standards Manual)	29

Section 9: Other Issues (ADR, Ombudsperson, Applicant Training/Certification) 	30

Section 10: Transition Tasks and Plan	31

Appendices

Appendix A: Working Group Membership and Participation	33

# Section 1: Introduction, Background, and Overview

Introduction and Process Overview

The Massachusetts Distributed Generation Interconnection Working Group (“Working Group”) was initiated at the request of the Massachusetts Department of Public Utilities (“DPU”) through Order 11-75.   In that Order, the DPU detailed its expectations for the Working Group as follows:

“The original DG Collaborative established uniform standards for the interconnection of distributed generation in the wake of the restructuring of the electric industry.  D.T.E. 02-38, at 1-2.  Building on this foundation, the goal of the Working Group here is to determine what changes should be implemented to ensure an efficient and effective interconnection process that will foster continued growth of distributed generation in Massachusetts.  The Department notes that the Working Group should not endeavor to recreate or reconvene the DG Collaborative, but rather should focus on the issues that need to be addressed in order to update the existing generation interconnection framework.” [D.P.U. 11-75-A, at 4]

“The goal of the Working Group is to reach consensus on distributed generation issues.  However…consensus may not be attainable on some issues and additional Department process may be necessary, including a possible adjudicatory proceeding.” [D.P.U. 11-75-A, at 5]

“The Working Group should consider the issues presented in the DG Report, DOER Petition, comments filed in this proceeding, and any other related issues determined relevant by the Working Group…Accordingly the Working Group is directed to (1) determine what issues should be resolved regarding the current distributed generation interconnection standards and application procedure to ensure an efficient and effective interconnection process, and (2) deliberate with the goal of reaching a consensus on a resolution of such issues for Department review and approval.” [D.P.U. 11-75-A, at 7]

Twenty organizations actively participated throughout the four-month facilitated Working Group process.  These organizations are listed below in four separate clusters:

- DG Providers,

- Utilities,

- State Agencies, and

- Customers/Cities.

Appendix A presents a full roster of all the participants from each organization that participated in the Working Group.

The Massachusetts Clean Energy Center provided funding for the facilitated Working Group process.  Dr. Jonathan Raab facilitated the process, with assistance from Susan Rivo also from Raab Associates, Ltd. and Walker Larsen from CLF Ventures. The Working Group’s first meeting was held on May 31, 2012.  Both the National Renewable Energy Laboratory (NREL) and the Interstate Renewable Energy Council (IREC) participated in the process as outside experts and provided technical assistance on a wide range of issues.

The Working Group met in plenary for ten days of meetings over the course of four months.  In addition, two Subcommittees (one focusing on technical issues and the other focusing on process, timeline, and fee issues) met consistently throughout this period to develop detailed proposals for review by the full Working Group during its plenary sessions.

With this report, the Working Group has completed its recommendations on issues identified by the Commission in DPU 11-75, as well as on additional but related issues identified by the Working Group participants.  These recommendations represent a consensus of the diverse members of this Working Group.  This report also includes a transition plan and a strategy for ongoing collaboration within the next nine months to ensure that the plan is implemented.

Summary of Findings and Recommendations

The current Massachusetts DG Interconnection Tariff was the result of a similar collaborative stakeholder process in 2002 and 2003.  During the first five or so years after the tariff was approved by the DTE (precursor to the DPU), the tariff allegedly functioned fairly well—the utilities were able to meet the timelines in the tariff and applicants were interconnected in a timely fashion.  Over the past few years, there has been a sharp increase in the number of DG applications as a result of falling technology costs (e.g., Photovoltaics or PV) and an increasingly favorable policy regime in Massachusetts for distributed generation (e.g., net metering, SRECs).

The increase in the sheer volume of applications has been coupled with an increase in the size and complexity of many of those applications, as well as an increasing concentration (and saturation) of DG in certain areas, necessitating additional review and analysis prior to interconnecting.  While utilities have been increasing their staff and outside contractors to handle the increased workload, it does not appear that they have been able to consistently meet the timelines in the tariffs, especially for projects going through the Expedited and Standard tracks.  However, it appears the delays in the interconnection process are not all on the utility side.  Applicants often submit many more applications than they intend to pursue as a way of reserving a place in the queue, and then sort through which applications will be most cost effective once the relative interconnection costs become clearer.  Oftentimes it is the applicant not responding to utility requests for additional data, clarification, or a signature, that is responsible for the time delay.

Because the monthly tracking data supplied by the utilities to DOER only captures dates that applications are deemed complete and dates when an interconnection agreement is sent (as per prior negotiated agreements), it is unclear where applicants are in the review process and whether projects that appear to be taking longer than the timelines allow, are delayed because of applicant delay, utility delay, or both.  Hence, the over 600 MW of DG still awaiting an interconnection agreements in the Expedited and Standard tracks (shown in the figure below) constitute a mix of stale projects that the applicants do not intend to pursue and live projects—many of which have exceeded applicant or utility deadlines.

While the number of applications in the Simplified process has also increased substantially over the last few years, the utilities have largely, but not entirely been able to meet the15 day timeframe they are given by the tariff.  According to the utilities’ presentation at the first Plenary session of this Working Group, of the nearly 5,000 applications received by all the utilities between January 2009 and the end of the first quarter of 2012, 91% were completed within the 15 day timeframe.  In 2011, however, only 75% of the applications were completed in 15 days.

The Working Group assessed the realities of the current DG interconnection timelines and developed the recommendations delineated in this report to address the identified problems.   The changes recommended by the Working Group in this final report include:

- Revisions to the technical screens and Supplemental Review time budget to potentially allow more projects to qualify for both the Simplified and Expedited tracks

- A required Pre-Application Report for applicants to the Expedited and Standard tracks to help applicants prioritize among potential locations and DG configurations (and reduce the number of speculative applications)

- A new group (cluster) study process for handling multiple applications on exhausted or near-exhausted feeders that will likely require substantial upgrade costs

- Additional time within the Standard track for “Complex” applications, that will require more analysis and hence more time than a typical Standard track project

- A more clear-cut and definitive process for utilities to withdraw project applications when applicants miss deadlines to provide information or other documents, thus freeing up feeders for other applicants and reducing utility workload (aka stale project management)

- A multi-faceted utility timeline assurance and enforcement strategy

- Utility-run chess-clocks to monitor both utility and customer timelines from the initial pre-application report through the application process to construction/interconnection. Enhanced monthly reporting to DOER on timelines.

- Utility published technical criteria and standards manuals that are periodically updated

- Other (that rises to this level of importance?)

Report Structure

Section 2 of this report lays out the Working Group’s recommendations for the application review process, including revised screens, a potential new “complex project” track, and recommendations for a group/cluster study process.   Section 3 provides recommendations for application and construction timelines, including timelines for the potential “complex project” track and cluster studies.   In Section 4, we outline recommended measures to ensure adherence to timelines for both utilities and DG applicants.  Section 5 covers application fee updates and potential to assign operation and maintenance costs for large projects to DG customers.   Section 6 outlines recommendations for a new pre-application report process. Section 7 outlines the recommendations for a new online application and project tracking system.  Section 8 describes technical issues, including a standards manual, while Section 9 describes recommendations for other issues, including a potential ombudsman and application training. Section 10 concludes the report with a transition strategy and recommendations for ongoing collaboration.

The appendices contain important additional documents.  What should go in the appendices?

Section 2: Application Review Process: Tracks and Revised Screens

The Working Group recommends changing several screens in the Simplified and Expedited tracks as well as increasing the number of engineering review hours within the Expedited track with the express purpose of allowing more projects to remain in these tracks and hence move more rapidly through the interconnection process.  The Working Group also recommends additional time for more complex projects within the Standard track.  Lastly, the Working Group recommends the addition of a Group (aka Cluster) track for multiple applications on feeders that are relatively saturated with distributed generation such that very expensive upgrades would be necessary.  The Group track would allow the utility to study multiple projects at once and establishes study and construction cost allocation approach

- Simplified Track

The Working Group recommends increasing 10 kw single phase maximum size to 15 kw and leaving the three phase maximum size at 25 kw. Moreover, the Working Group recommends keeping projects that fail screen #5 in the Simplified Track rather than moving them to the Expedited Track, but allowing the utilities to have a total of 20 days to review those applications rather than 15 days.

- Simplified and Expedited Track/Screen #2

The Working Group recommends changing one of the existing screens (Is the aggregate generating Facility capacity on the circuit less than 7.5% of circuit annual peak load?) to potentially allow more DG thru the Simplified and Expedited tracks, as follows: Is the aggregate generating Facility capacity 15% of feeder/circuit and, if available, line segment?

- Simplified Spot Network Track/Screens

Utilities are studying area networks to develop the data needed to come up with appropriate/safe screens for area networks. For now, the Working Group recommends that the simplified spot network screens also apply to area networks (if other screens are passed) as long as applicant has interval meter data for an appropriate time period, and where available minimum load data, for area networks. The Working Group further recommends removing the requirement that the system be less than or equal to 15 kw, as long as the less than 1/15 of Customer’s minimum load is met.  The Working Group also recommends continuing to monitor and track IEEE 1547 and national best practices and for the Massachusetts utilities to continue to study and experiment on area networks (e.g., NSTAR pilot project).  They further recommend incorporating networks and IEEE handling of networks into new technical upgrade criteria and standards manual discussed in Section X.

- Expedited Track Screens

The Working Group recommends adjusting the Expedited track screens to allow more applications to remain in the Expedited track instead of going through the longer Standard track.  Specifically the Working Group recommends adding three Supplemental Review screens to the interconnection process and to increasing the amount of engineering hours allowed for Supplemental Review before a project is moved from the Expedited to the Standard track from 10 hours to 30 hours.

The three screens to be added to the Expedited Track are:

- Penetration Test

- Power Quality and Voltage Tests

- Safety and Reliability Tests

The Supplemental Review consists of Supplemental Review Screens A through C.  If any of the Screens are not passed, a quick review of the failed Screen(s) will determine the requirements to address the failure(s) or that an Impact Study is required.   In certain instances, Distribution Provider may be able to identify the necessary solution and determine that Detailed Studies are unnecessary. Some examples of solutions that may be available to mitigate the impact of a failed Screen are:

1.	Replacing a fixed capacitor bank with a switched capacitor bank.

2.	Adjustment of line regulation settings.

3.	Simple reconfiguration of the distribution circuit.

Screen A: 	Penetration Test

Where 12 months of line section minimum load data is available, can be calculated, can be estimated from existing data, or determined from a power flow model, is the aggregate Generating Facility capacity on the Line Section less than A) 67% (Plus evaluate over next 18-24 months moving to 100% minimum screen.) (Utilities) or  B) 100% with exceptions on transition basis (DG & others) of the minimum load for all line sections bounded by automatic sectionalizing devices upstream of the Generating Facility?

	If yes (pass), continue to Screen B.

	If no (fail), a quick review of the failure may determine the requirements to address the failure; otherwise either a Group Study or an Impact Study is required.  Continue to Screen B.

Note 1: The type of generation will be taken into account when calculating, estimating, or determining circuit or Line Section minimum load relevant for the application of this screen. Solar generation systems with no battery storage use daytime minimum load (i.e. 10 am to 4 pm for fixed panel systems and 8 am to 6 pm for PV systems utilizing tracking systems), while all other generation uses absolute minimum load.

Note 2:  Distribution Provider will not consider as part of the aggregate generation for purposes of this screen Generating Facility capacity known to be already reflected in the minimum load data.

Significance:  Penetration of Generating Facility installations that does not result in power flow from the circuit back toward the substation will have a minimal impact on equipment loading, operation, and protection of the Distribution System.

Screen B:  Power Quality and Voltage Tests

In aggregate with existing generation on the line section,

a)	Can it be determined within the Supplemental Review that the voltage regulation on the line section can be maintained in compliance with current voltage regulation requirements under all system conditions?

b)	Can it be determined within the Supplemental Review that the voltage fluctuation is within acceptable limits as defined by IEEE 1453 or utility practice similar to IEEE1453?

c)	Can it be determined within the Supplemental Review that the harmonic levels meet IEEE 519 limits at the Point of Common Coupling (PCC)?

	If yes to all of the above (pass), continue to Screen C.

	If no to any of the above (fail), a quick review of the failure may determine the requirements to address the failure; otherwise a Group or Impact Study is required.  Continue to Screen P.

Significance:  Adverse voltages and undesirable interference may be experienced by other Customers on Distribution Provider’s Distribution System caused by operation of the Generating Facility(ies).

Screen C:      Safety and Reliability Tests

Does the location of the proposed Generating Facility or the aggregate generation capacity on the Line Section create impacts to safety or reliability that cannot be adequately addressed without a Group or Impact Study?

	If yes (fail), review of the failure may determine the requirements to address the failure; otherwise a Group or Impact Study is required.  Continue to

	If no (pass), Supplemental Review is complete.

Significance: In the safety and reliability test, there are several factors that may affect the nature and performance of an Interconnection.  These include, but are not limited to:

1.	Generation energy source

2.	Modes of synchronization

3.	Unique system topology

4.	Possible impacts to critical load customers

5.	Possible safety impacts

The specific combination of these factors will determine if any system study requirements are needed. The following are some examples of the items that may be considered under this screen:

1.	Does the Line Section have significant minimum loading levels dominated by a small number of customers (i.e. several large commercial customers)?

2.	Is there an even or uneven distribution of loading along the feeder?

3.        Is the proposed Generating Facility located in close proximity to the substation (i.e. <2.5 electrical line miles), and is the distribution line from the substation to the customer composed of large conductor/cable (i.e. 600A class cable)?

4.        Does the Generating Facility incorporate a time delay function to prevent reconnection of the generator to the system until system voltage and frequency are within normal limits for a prescribed time?

5.	Is operational flexibility reduced by the proposed Generating Facility, such that transfer of the line section(s) of the Generating Facility to a neighboring distribution circuit/substation may trigger overloads or voltage issues?

6.	Does the Generating Facility utilize UL 1741/IEEE 1547 Certified anti-islanding functions and equipment?

The Working Group also recommends raising the Supplemental Review time allowed within the Expedited track from 10 hours to 30 hours.  Thus projects would be allowed to stay in the Expedited track and not sent to the Standard track if more than 10 hours of engineering review time is required.

- Complex Projects Within Standard Track

The Working Group discussed at length how to handle the increase of complex projects or projects seeking interconnection at challenging locations that require more studies and study time than initially contemplated when the Standard track and its timelines were designed.  The Working Group agreed to maintain the Standard Track, but to allow for additional utility review time in certain circumstances.  See Section 3 for details.

- Accelerating Interconnection Agreement Signing

The Working Group recommends adding language to the tariff that allows applicants to request and sign an Interconnection Agreement at the end of the Impact Study rather than waiting until after the Detailed Study.  If the applicant goes with this option they agree to accept the +/-25% construction cost estimates emanating from the Impact Study.  They also will have to wait for a detailed construction schedule until after the utility completes its design engineering work (as discussed in Section X under construction timelines).

NOTE: At end of Plenary #7 new idea floated to have everyone sign IA at end of Impact Study and live with +/- 25%--jetisoning the +/- 10%.

- Group (aka Cluster) Study

The Working Group recommends that that a new Group (aka Cluster) Study process should be required on feeders where capacity is “exhausted ” (technically infeasible to operate on a single distribution feeder, e.g., Grid’s 3 MW PV on a 15 KV line 5 MW on 25 KV line) (or near exhausted), or where new express feeder is needed, or both.   The Group study would also be optional in other circumstances identified by utilities as potential good candidates for Group studies, or proposed by applicants.

- Required Group Study Process

  - Utility decides when application triggers exhausted feeder, and  Option 1: that opens up group study window; Option 2: next applicant has option to proceed on own or move to group study]

  - Group study process is then required for all applicants wishing to interconnect on the feeder

  - Open enrollment window for 3 months

  - Timeline for utility: Option 1: mutually agreed to timeframes; Option 2: Complex study timeline, or mutually agreed to

  - Must follow cost allocation rules for Group studies (recommended by Working Group in Section X of this Report)

- Optional Group Study Options

  - Optional in other circumstances if applicants come together and propose to utility, or utility identifies other areas where Group studies may benefit applicants

Section 3: Application and Construction Timelines

In this section the Working Group recommends changes to timelines for Complex projects within the existing Standard Track and timelines for the new Group study process.  It also recommends clarifying language and some modifications to the related to witness test and construction timelines, as well as new language regarding force majeure.  [Add Simplified reference if changes.]

- Simplified Track

The Working Group recommends keeping the total utility review time at 15 days but allowing the utilities 5 extra days for applications that fail Screen #5 in order to keep those applications in the Simplified Track rather than moving them to the Expedited Track.

- Expedited Track

The Working Group does not propose any changes to the Expedited timelines, except to clarify the timing in the Witness Test (see below in this section).

- Complex Projects in Standard Track

The Working Group recommends adding additional time within the Standard review track for complex projects or projects proposing to interconnect in challenging places.  These types of projects typically require more expensive system upgrades that necessitate more study time than Standard track timelines afford.  Therefore for these types of projects or situations the Working Group recommends:

- If any Sub-Station modifications  are needed(i.e., adding or replacing equipment)—Add a maximum of 10 or 20 business days for utility to complete the Impact Study

- If system modifications from the Impact Study indicate likely to cost over $150,000 or $300,000  in EPS upgrades not including service upgrades for customer site —Add a maximum of  25 or 45 days for Detailed Study (Add diagram or more delineated language.) (See page in report for illustrative costs)

- Utilities will inform applicants within 20 days into Impact study whether 1, 2, or both time extensions are needed

Consider IA after Impact Study for everyone with +/- 25%, then do Detailed Study and give Construction schedule (and drop the +/- 10%).  Can that reduce any timeframes?

- Group (aka Cluster) Study

The Working Group recommends that where a Group study is implemented whether required by utilities or voluntary the study timeframe should be by mutual agreement between the utility and the Group members.

- Construction Timelines

The Working Group recommends that there should continue to be clear construction timelines w/milestones included in the Interconnection Agreement (except in the case where Applicant requests an Interconnection Agreement after the Impact Study and before a Detailed Study, in which case the construction schedule is added after the utility completes its design engineering).  They further recommend the timelines be tracked using a chess clock just as with the interconnection agreement steps.  While the Working Group recognizes that there are many reasons that construction schedules may slip on both the applicant and utility side, milestones should only be missed for reasonable cause.

If a utility misses a milestone it will inform both the applicant and the DPU including the reason and a proposed new schedule.  If the customer misses a milestone, the utility will follow the same protocols for Customer Adherence to time schedules described below in Section 7.

The Working Group also recommends that construction time guidelines for different upgrade costs and timeframes be included in the Technical Manual referenced in the tariff, and periodically updated, with stakeholder   input and review (see below for illustrative example—note if multiple upgrades required some can be done concurrently so timelines not necessarily additive).

- Force Majeure

The Working Group recommends that for force majeure (as defined below) that the chess clock would be stopped for that period (for the utility, customer, or both depending on who’s impacted by the force majeure). There should be notice when force majeure events occur. Volume of applications would not be force majeure. [Also, the Working Group agrees to delete language in tariff about complying with timelines only under “normal work conditions”].

The term “Force Majeure Event” as used herein, shall include, but not be limited to, any act, omission, or circumstance occasioned by, or in consequence of, any act of God, act of the public enemy, war (declared or otherwise), acts of terrorism, sabotage, invasion, riot, fire, , flood, or other natural catastrophes, ice, explosion, a major weather event as defined by the Company's Service Quality Plan,  , failures to act or orders of any kind of any governmental authority acting in its regulatory or judicial capacity, strike, labor dispute, or any other cause or circumstance beyond the reasonable control of, and not resulting from the fault or negligence of, the party claiming the occurrence of a Force Majeure Event.  Nothing in this provision is intended to excuse a distribution company’s performance due to any governmental act, failure to act, or order, where it was reasonably within such distribution company’s power to prevent such act, failure to act, or order.  Notwithstanding anything in this tariff to the contrary, Force Majeure shall not mean: (i) acts or orders of any kind of governmental authority that increase the aggregate net metering capacity of net metering facilities in the distribution company’s service territory; or (ii) acts or orders of any kind of governmental authority that increase the eligible generating capacity of a net metering facility in the distribution company’s service territory.

If there is a major (and abrupt) change in State or Federal policy or DG price change that prompts significant and rapid increase in applications, Utilities will use best efforts to adjust (human) staffing/resources to handle the new application volume within the tariffed time lines.  If they can’t staff up rapidly enough to meet the timelines, they will let the DPU know and file a plan to meet the deadlines as expeditiously as possible.  Utilities and DG related stakeholders will work together to anticipate these types of changes, and minimize their impacts on the interconnection process.

[Note: Consider moving elsewhere?]

- Witness Test

The Working Group recommends adding language to the Tariff to clarify Witness Test procedures and timelines as follows:

- Simplified: Leave Language as is Section 3.1 (Item F)

- Expeditid: Add new section for Expedited—Identical Language as Simplified

Standard: (Replace Section 3.3.3.B.i with the following) The Company will require a witness test of the Facility for compliance with the relay settings as approved by the Company. The Interconnecting Customer will provide a proposed witness test and the requisite supporting documentation for review by the Company once they have completed the installation of the facility. Utility will have 5/10 business days to approve the witness test once they have all the information needed from the Customer.  The utility will then inform the Customer when they have approved test procedures. Once the test has been approved by the Company, the Interconnecting Customer will call to arrange for the Witness Test. The Interconnecting Customer has no right to operate in parallel until a Witness Test has been passed. The Company is obligated to complete this Witness Test within 10 business days or by mutual agreement upon receipt of the request for a witness test as outlined above.

Section 4: Adherence to Utility and Applicant Timelines

In this section the Working Group recommends strategies and requirements to enhance adherence to timelines during the application and construction phases of distributed generation interconnection—on both the applicant/customer and utility sides.

- Applicant/Customer Adherence (aka Stale Project Management)

The Working Group recognizes the need to remove stale projects that have exceeded their timelines to provide utilities with requested information or decisions to proceed.  Stale projects can hold up other projects behind them in a queue on a particular feeder.  However, even when there is not a queue, stale projects still require utility tracking and periodic attention, and also can give the misconception that many projects are actively awaiting interconnection.  For all these reasons, the Working Group proposes a process that includes an initial withdrawal of stale projects, as well as an on-going customer timeline compliance process to deal with applicants who miss their deadlines, as outlined below.

- Initial Withdrawal

  - For all applicants where the utility is waiting to hear from the customer at any level at any stage (in application and construction process) for more than 30 business days

  - Utility contacts applicant (email and letter and/or phone if no email address)—customer of record, alternative contact, and a most recent point of contact

  - “Haven’t heard from you in over 30 business days, if don’t hear from you in 30 business days, we will consider your application withdrawn (and if you want to continue at a later date, you will need to reapply).”  Any fees not refunded.

  - (Indicate removal being required by DPU)

  - Utilities already have the authority in the original tariff—“may” remove from queue

- On-Going Customer Timeline Compliance (for all projects whether in a queue or not)

  - Request from utility to applicant for information or signature will include customer deadline from tariff

  - If miss deadline, send email that missed deadline and will be given 10 business days to cure or request an extension

  - If request extension, granted one extension equal to timeline/deadline of step, unless otherwise authorized as follows::

    - Two times prior to the distribution company’s provision of an Interconnection Service Agreement to the Customer, the Customer may request an additional extension period of 60 Business Days if a Customer cannot meet a request for information related to the engineering studies and reviews being performed by the distribution company within the customer deadline timeframe because the information requested is held by a third party (i.e., equipment manufacturer) and such information cannot be obtained by such Customer despite reasonable efforts to do so.  There shall be no fee for an extension under this provision.

    - During any course of the interconnection process, a Customer may request an additional extension period of 60 Business Days provided that such Customer has submitted a fee of $2.00/kW, such fee to be credited toward interconnection costs for project or lost if project does not move forward.  Requests for this extension period shall be limited to one time for solar projects and five times for technologies other than solar.

    - One time, during any course of the interconnection process, a Customer may request an additional extension period of six months for legal challenges related to a Facility.  The Customer shall submit a Certification that a governmental permit or approval for the Facility is subject to a legal challenge prior to the Customer deadline or during the initial extension period and the legal challenge remains pending.  This additional extension period for legal challenges terminates at the end of the legal challenge or six months after the first day of this additional extension period for the legal challenge, whichever comes first.  There is no fee for an extension under this provision.

    - One time, during any course of the interconnection process, a Customer of a Public Facility may seek an additional extension period of six months by certifying to the distribution company one or more of the following: (1) a town meeting vote required for the Public Facility; (2) special legislation required in relation to the Public Facility; or (3) any approval for the Public Facility necessary under Article 97 of the Massachusetts Constitution.  The additional extension period for Public Facilities shall terminate at the end of the governmental process specified above or six months after the first day of the additional extension period for Public Facilities, whichever comes first.  There is no fee for an extension under this provision.

    - The following definitions shall apply to this provision:

      - “Certification” means a written statement based on knowledge, information, and belief that the relevant claims are true.

      - “Public Facility” means any Facility (1) that is owned or operated by a municipality or other governmental entity; or (2) that is sited on land of a municipality or other governmental entity; or (3) of which for purposes of Net Metering, qualifies as a net metering facility of a municipality or other governmental entity.”

    - If clock stoppage for customer request for extension near end of window, utilities can get extension for cause; or if multiple customer requests for extensions project removed from tracking for SQM calculations.

  - Utilities will keep track of extension dates

  - Projects that don’t meet extended timelines considered withdrawn, need to reapply

  - Customers will have 20 business days to sign an Interconnection Agreement by the utility or provide comments to the utility on the IA, or the project will be considered withdrawn and will need to reapply.  If customer provides comments, the customer and the utility will have 30 business days to resolve.  After 30 days, if no resolution and no request from the customer for ADR, the application will be considered withdrawn and need to reapply.

  - Customers shall not be required to pay any costs related to distribution company infrastructure upgrades or system modifications upon execution of the Interconnection Service Agreement (or once they get the Construction schedule).  Customers shall have six months from the date of execution of an Interconnection Agreement to pay 25 percent of those costs.  If a Customer pays such cost within the six month timeline, the Customer shall have an additional six months from the date of first payment to pay the remainder of the costs.  In the event that Customer fails to pay the distribution company within the timeline required by this provision (or within any extension to such timeline as authorized under Section 1(iv) and 1(v) above), the distribution company will require the Customer to reapply for interconnection. Construction schedule will commence once applicant financial commitment/payment made.

- Timeline (after DPU approval)

  - Initial Withdrawal—Begin right after DPU approval (2-3 months to complete)

  - On-Going Customer Timeline Compliance—Concurrently w/Initial withdrawl or after/sequential?

- Utility Adherence (aka Assurance and Enforcement) to Timelines

The Working Group recommends a suite of measures to ensure and enforce utility compliance with tariff timelines.

- Service Quality Metrics:

The Working Group believes that it is appropriate to explore the design of a service quality metric associated with enforcing timelines established in the Standards for Interconnection of Distributed Generation through a proceeding at the D.P.U.  Moreover, the utilities agree not to oppose the inclusion of such a metric in the context of such proceeding and have the metric be approved for effect as of January 1, 2014.  The Working Group believes that the specific design of such metric including but not limited to benchmarks and overall weighting should be discussed in the context of the aforementioned D.P.U. proceeding.

Note following Sentence Also in Play: Moreover, the utilities support discussion of other comparable proposals relating to enforcing interconnection timelines in the context of this proceeding.

- Refunding Application Fees for Expedited and Standard Processes When Timelines are Missed (Note: This and E below would be an interim measure to begin asap and last only until SQM are “fully operational”.  C & D below would be on-going even after SQM was fully operational)--

  - after the IA is delivered or the total utility review time appears to be exceeded the customer has 20 business days to ask for a review of timeline  adherence

  - the utility will have 10 business days to provide documentation of timeline adherence as compared to the total times allowed for the study track followed

  - if utility has not adhered to the utility timelines, the utility will process a refund of the customer’s application fee within a month.

  - the customer has 10 business days to appeal the utility review asking for an Ombudperson’s decision as outlined below

  - Shareholders cover refund [Remove from report?]

- Expedited Process at DPU/ADR Process/Ombudsperson (technical and other issues only)

  - look for DOER/DG suggestions

  - Customer would file complaint on a technical issue within the process to the Ombudsperson and the utility. The utility would have 10 business days to respond to the customer and DPU.

  - If the utility response does not have specific technical background as per good utility practice, then the matter would be taken up by the Ombudsperson

  - The ombudsperson would respond in 20 business days and their response must conform to good utility practice.

  - The decision of the ombudsperson can be appealed thru the normal complaint appeal process as the DPU

  - Include comment/complaint form

  - How Obmbuds paid for?

  - Who should Ombuds answer to?

- Missed Deadline Notification and Timeline Revision

  - a customer may request review of timelines in the process at anytime or if deadline is missed at each stage

  - utility will provide a written (email) response to the request within 10 business days detailing the reason for the  missed timeline and the expected date the process step will be completed

  - the DPU can at any time request additional information as to the specific missed timeline or a pattern of missed timelines

  - consider when and if  clock stops, and what if anything should go to Ombuds/ADR process

- Annual Reporting and Review of Utility timeline compliance based on tracking system (at least until SQM kicks in)

Section 5:  Fees

The Working Group recommends updating the fees for the Expedited and Standard processes to account for actual labor rates and anticipated review times. We also lay out cost allocation approach for new Group study process.  Actual costs will still be charged for Impact Studies and Detailed Studies. [Add language about Simplified and O&M if have recommendation.]

- Required Pre-Application Report Fees (Expedited/Standard Track Only)

The Working Group recommends that there be no fee for Pre-Application Report, but that the anticipated cost was taken into account when setting the new application fees for the Expedited and Standard processes.

- Simplified Track

The Working Group recommends that there continue to be no fee for Simplified applications, but that the cost of reviewing the Simplified applications be taken into consideration when setting the application fees for the Expedited and Standard application process.

- Expedited and Standard Tracks

The Working Group agrees that current Expedited and Standard application fees are in need of updating and do not appear to be fully covering utility costs to review applications.  Therefore, the Working Group recommends that the D.P.U. review the recent historic costs and take into consideration anticipated changes to the application process (e.g., pre-application report) in setting fees that reflect actual review costs.

In the interim, the Working Group recommends that the utilities should immediately increase the application fees for the Expedited and Standard to $4 per kw, with a maximum application fee of $7,500, and that the rate for Supplemental Review engineering hours be increased from $125/hour to (set in 2003) to $150/hour

- Group (Cluster) Study and Upgrade Cost Allocation (repeated from Section 6)

The Working Group recommends that the cost allocation for study and upgrade costs when a group (cluster) study is either required by the utility or a voluntary group (cluster) is established should be as follows:

- Study Cost Allocation—by MW

- Upgrade Cost Allocation

  - Lines—Share common segments pro rata by MW, unique segments covered by that DG provider

  - Other equipment—Share common upgrades pro rata by MW, unique upgrades by that DG provider

  - If one or more DG applicant drops out, then remaining applicant share any additional restudies required

  - If new DG added to circuit within 5 years, need to share costs from prior DG (consistent w/utility line extension policy).  However, new applicantss through the Simplified process would be exempted from this requirement.

- Operation and Maintenance Costs

The Working Group acknowledges that O&M costs on utility upgrade equipment are not currently being assessed on existing DG customers. And…[Utilities need to decide whether will be requesting this or not.  DG et al clear will not support O&M]

Section 6: Pre-Application Report Requirements

The Working Group recommends adding a new required Pre-Application Report for all applicants going through the Expedited and Standard Tracks that are over 500 KWs, and optional for under 500KW.  The intent of this Report is to provide applicants with some basic information about the location at which they are potentially interested in connecting to the distribution system, so that they can get an initial sense of whether the particular location is practical for their project.  The pre-application report could also help applicants prioritize among various locations and possible distributed generation configurations they are considering.  The Working Group believes that this could minimize the number of speculative applications, and increase the likelihood of viable applications.

Utilities would have 10 business days to provide the pre-application report.  There would be no fee for this service (however costs reflected in application fees).  Applicants would not be able to submit their actual application in the Expedited and Standard Tracks until a pre-application report is received.

Each Pre-Application Report will carry the following disclaimer: “Be aware that this Report is simply a snapshot in time and is non-binding, system conditions can and do change frequently.”

Applicants would need to provide the following information to the utility through the statewide online application and tracking system:

- Project Contact Information

Name:

Address:

Phone:

Email:

- Location (street address with nearby cross streets, town):

- Generation Type: (solar, wind, CHP)

- Size (AC kWs):

- Single or three phase generator  configuration:

- Stand-alone (no on-site load – Y or N):

- If existing service include customer account number, site minimum and maximum (if available) current or proposed electric loads in kWs

- New service needed?

The “Pre-Application Report” provided by the utility will include the following.

- Circuit voltage:

- Circuit name:

- Voltage at proposed location:

- Single or three phase available near site:

- If single phase – distance from three phase service:

- Aggregate connected  DG (kw) on circuit:

- Submitted complete applications of DG (kw) on circuit that have not yet been interconnected:

- Area network, or spot network or radial:

- Snap-shot within ¼ mile (or otherwise identify feeders within ¼ mile)

- Other potential constraints or critical items that may jeopardize project

Section 7:  Information Tracking and Reporting

The Working Group recommends that each distribution company establish its own chess clock tracking system for applications.  The chess clock would track both the utility and customer time within each stage in the application, construction, and witness test as well as the overall utility time elapsed for the application and construction processes. This timeline tracking system would be used for multiple purposes including but not limited to informing applicants about where they stand in the application process, enforcing the stale project management procedures, monthly reporting to DOER, and for any Service Quality Metrics put in place by the D.P.U.

The distribution companies agree to implement the chess clock and monthly reporting plan that will include the following elements:

- Chess clock to track customer and utility elapsed time in each stage of application through construction and witness testing

- Updating monthly reporting to DOER to include

  - Start and end dates for each stage, and elapsed utility time for each stage

  - Feeder ID numbers for each project

- Distribution Companies will implement over the next 6-8 months as follows

  - Within 1-2 months for all new applications

  - Within 1-2 months all applications that move to a new stage (these will only be tracked for that stage and further stages, but not back)

  - Within 6-8 months other existing and live projects following initial withdrawal of stale projects (from current stage forward)

- Other Questions for WG Participants—What Are We Now Proposing About Training and Online Applications???

  - Training—applicants for going through the application processes.  Should there also be verification/certification?

  - Centralized Application process

    - Pre-application Report for Expedited and Standard tracks

    - Application--Centralized/Standard application process for all 3 tracks (update interconnections applications)

Section 8: Other Technical Issues (including Upgrade Criteria and Standards Manual)

- Upgrade Criteria and Standards Manual

The Working Group recommends that utilities develop and make available upgrade criteria and standards manuals based on National Grid’s “ESB-756C”, with the following recommendations:

  - Add information on  infrastructure/system modifications upgrade criteria to manual including costs/timelines and triggers

  - Update manual on an as needed basis with maximum of 3 or 5 years w/stakeholders (DG providers, state agencies, customers) input

  - Option 1: One statewide manual, even if has to be some differences within that document among the utilities [If this way who’s responsible for updating/maintaining?]  Option 2: Each utility has own manual—but structure and content as close as possible

  - Establish a DG interconnection technical advisory committee that meets 3 times per year to review technical issues related to DG interconnection (including new technology, criteria, and standards), and to review and comment on any proposed modifications to the Standards Manual.  Advisory Committee to be comprised of 3 non-utility members with technical expertise on DG interconnection. Advisory committee would also include representatives from all the utilities and Ombuds from DPU.

  - As part of the transition effort, utilities will compare their standards w/GRID’s and have process laid out including schedule for developing manual(s)

Below is original DG et al request:

- Standing technical standards review board that meets quarterly.  Any changes to the manual must be approved by a majority vote of the board.

- 7 member Board, with 4 utility representative and 3 non-utility representatives made up of engineers with DG interconnection experience.  In other words, the utilities can always win a vote, but...

- Non-unanimous votes earn a footnote in the manual saying that there was dissent.

- When a utility goes outside the manual, they have to explain to the DPU why if requested by the customer, and that decision is subject to the ADR process (that doesn't technically need to be called out specifically since there is no definition of what is and isn't subject to ADR in the tariff, but nevertheless it's worth pointing out.)

- Review and comment on changes in advance of implementing

Section 9: Other Issues (ADR, Ombudsperson, Applicant Training/Certification)

Alternative Dispute Resolution Process (ADR)

The Working Group  acknowledges that the ADR process for DG at the DPU has largely been untested over the past decade. As such, the only change related to the ADR process that we are recommending is the addition of an Ombudsperson as described below.

Ombudsperson

The Working Group recommends that the DPU name a staff DG Ombudsperson with technical expertise and authority to effectively carry out the following duties;

- ADR;

  - Ombudsperson role -- The Ombudsperson would hear –in confidence?? – the complaints of parties that reach the end of Step 9.1 Good Faith Negotiation without resolution. The Ombudsperson would a) be easily accessible; b) review the written documentation from Step 9.1; c) conduct independent interviews/ investigations as deemed necessary; d) offer independent problem-solving assistance from a third-party vantage.

  - Ombudsperson’s judgments -- The intent of the Ombudsperson is to resolve issues as expeditiously as possible. The Ombudsperson could a) propose a solution (non- binding); b) render a judgment about whether the issues are best resolved through i) an informal settlement; ii) other alternative means (e.g., informal negotiation before an expert third party); or iii) continued use of the DR process. If the latter, the Ombudsperson could also advise whether the dispute should pursue Step 9.2 Mediation/ Informal Arbitration, or go directly to 9.3 Departmental Hearing.

- Reporting -- Quarterly reports will be issued to the DPU summarizing the actions of the Ombudsperson; specific attention will be given to reoccurring issues for both utilities and developers.  An annual report will be issued summarizing the interconnection process, highlighting areas of concern.

- Technical Standards – Ombudsperson will participate in the review and modification of the Technical Standards Manual

Training

The Working Group recommends changing the monthly “briefing” into more of a “training” that may or may not include some form of applicant certification. The trainings would provide an opportunity for applicants and utilities to interact, and could be a mandatory part of the application process. This could also link into any future online application process that requires applicants to take and pass a “how to apply for interconnection” test before submitting the online application.  Details to be worked out in on-going collaborative process.

Section 10: Transition Tasks and Plan

Working Group is recommending the following transition strategy over the next year to assist in the implementation of the recommendations in this Report.

Transition Tasks (with estimated timeframe)

- Redline tariff (less than one month)

- Establish DG Interconnection Technical Advisory Committee (2 months)

  - Compare utility standards w/GRID’s and have process laid out including schedule for developing manual(s) (one month)

  - Plan for monitoring IEEE 1547 and national best practices (3 months)

- Chess-clock development and monthly DOER reporting upgrade—(1-6 months)

- Develop role for ombudsman and implement (3 months)

- Trouble-shoot during implementation of initial applicant withdrawal (4 months)

- Develop on-going trainings including online modules (6 months)

- Using outside Engineers during application and construction (1 year)

- Consider central administrator for tracking and application process (1 year)

- Consider accessible geographic mapping that will show feeders/circuits and DG activity (including names of sub-stations, circuits served) (1 year)

- Other?

Transition Plan Questions

- Meet weekly for first month (redlined tariff and chess clock) and then monthly thereafter?

- What needs to wait for DPU approval before starting, and what doesn’t?

- Who will participate from non-utility parties?

- Is facilitation support needed for transition period?  Any additional consulting support?

- Other?

Additional Language from DOER/Utilities on Issues Insurance and Tax Mark-Up

The Working Group agreed that a number of items need to continue to be addressed by the stakeholders after the filing of this report.  Primary among those issues are the following and the way the group plans for those issues to be addressed:

1) [placeholder] Technical Standards Manual (with a Standards Review Board)
[description of the decision-making process : meets quarterly : will address 3MW threshold, DTT requirement, RTU, and any other stakeholder proposals)]

2) DOER Recommendation TC-11: Insurance requirements – Prohibit requirements for additional insurance (DOER/IREC)

DOER believes additional insurance requirements are not necessary because the interconnection process adequately protects customer and utility property and adequately addresses electrical safety.  DOER asserts that FERC and other states do not have these additional insurance requirements.

Mass utilities believe that additional insurance is appropriately required to address potential third-party claims against utilities for damages caused by underinsured DG facilities.

The Utilities and DOER agreed there was not adequate time in the DG Working Group schedule to adequately address this issue.  The Utilities and DOER agreed to convene a discussion with respective insurance experts and legal counsel to discuss resolution of this issue. DOER and the utilities will submit an update on these discussions no later than two months after the filing of the DG Working Group Report (or November 11, 2012). The review/update on such discussions may include proposals for revisions to the existing tariff.

3) DOER Recommendation TC-17: Interconnection Costs: Review requirement of the tax markup on upgrades for public entities. (state customer)

DOER believes that there should be a waiver of the DPU-mandated “tax adder” carrying charge imposed by utilities on customers who contribute (i.e. pay for) assets that ultimately become a part of utility plant (such as interconnection upgrades) for DG facilities owned by public entities, such as state hospitals, state universities, etc.

The Utilities believe that there should be no such waiver, since any amounts not collected from customers causing the imputed tax are ultimately recovered from other customers.

The Utilities and DOER agreed there was not adequate time in the DG Working Group schedule to adequately address this issue.  The Utilities and DOER agreed to convene a discussion with tax and legal experts to discuss resolution of this issue. DOER and the utilities will submit an update on these discussions no later than two months after the filing of the DG Working Group Report (or November 11, 2012). The review/update on such discussions may include proposals for revisions to the existing tariff.

Appendix A: Working Group Membership and Participation

MA DG Working Group - Active Representatives and Alternates

| Organization | Representative | Alternate |
| --- | --- | --- |
| DG Providers - Solar |
| Blue Wave Capital | Eric Graber-Lopez |  |
| Borrego Solar | Dan Berwick | Ryan Burrowbridge |
| Exelon/Constellation | Scott Edwards | Robert Flottemesch |
| My Generation Energy | Michael Stone |  |
| SEBANE/SEIA | Francis Cummings |  |
| Spire Solar Systems* |  | Michael O’Dougherty |
| DG Providers-- CHP |
| Northeast Clean Heat and Power Initiative | Bill Pentland (ClearEdge Power) | Ruben Brown (E-Cubed, LLC) |
| Harvard | Douglas Schmidt | Mary Smith |
| Prime Solutions |  | Henrietta De Veer |
| Source One/Veolia | Reid Sprite | Larry Plitch |
| Utilities |
| National Grid | Tim Roughan | Kevin Kelly |
| NSTAR | George Moskos | Michael Brigandi |
| WMECO/NU | Cynthia Janke | Donald Wells |
| Unitil | Gary Miller | John Bonazoli |
| End Users/Cities/Towns |
| CLC/CVEC | Joseph Soares | Rebecca Zachas |
| State Agencies |
| MA AGO | Jamie Tosches | Kevin Walsh |
| MA CEC** | Nils Bolgen | Martha Broad |
| MA DOER*** | Gerry Bingham | Dwayne Breger |
| *Erik Hoagland was the alternate for Solar Spire Systems until 8.20.12 **Peter McPhee attended one meeting as an alternate for MA CEC ***Courtney Feeley Karp was the third alternate for MA DOER until mid-August 2012 |

| Sign in Sheet MA DG Collaborative Working Group Plenaries | 5.31 | 6.13 | 6.28 | 7.12 | 8.1 | 8.23 | 9.5 | 9.6 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Representatives and Alternates |
| Abe | Jonathan | Nexamp (alt.) | DG Solar |  |  |  |  |  |  |  |  |
| Berwick | Dan | Borrego Solar | DG Solar |  | X | X |  | X | X | X | X |
| Bingham | Gerry | MA DOER | State Agency | X | X | X | X | X | X | X | X |
| Bolgen | Nils | MA CEC | State Agency | X | X | X |  |  |  | X | X |
| Bonazoli | John | Unitil (alt.) | Utilities | X |  | X | X | X | X | X | X |
| Breger | Dwayne | MA DOER (alt.) | State Agency | X | X | X | X | X | X | X | X |
| Brigandi | Michael | NSTAR (alt.) | Utilities | X | X | X | X | X | X |  |  |
| Broad | Martha | MA CEC (alt.) | State Agency |  |  |  |  |  |  |  |  |
| Brown | Ruben | E Cubed LLC (alt.) | DG-CHP |  |  |  |  |  |  |  |  |
| Burrowbridge | Ryan | Borrego Solar (alt.) | DG-Solar | X | X |  | X |  |  |  |  |
| Cummings | Fran | SEBANE/SEIA | DG-Solar | X | X | X | X | X | X | X | X |
| De Veer | Henrietta | Prime Solutions | DG-CHP |  | X | X | X | X | X |  |  |
| Edwards | Scott | Exelon/Constellation | DG-Solar | X | X | X |  | X |  |  |  |
| Flottemesch | Robert | Exelon/Constellation (alt.) | DG-Solar | X |  | X |  |  | X | X | X |
| Feeley Karp | Courtney | DOER | State Agency | X | X |  | X | X |  |  |  |
| Graber-Lopez | Eric | Blue Wave Capital | DG-Solar |  |  |  | X | X |  |  |  |
| Hoagland | Erik | Spire Solar Systems (alt) | DG-Solar | X | X | X | X |  |  |  |  |
| Janke | Cynthia | WMECO | Utilities |  | X | X |  | X |  |  |  |
| Kelly | Kevin | NGRID (alt.) | Utilities | X | X | X |  |  | X | X | X |
| McLaren | Robert | NuGen Capital (alt.) | DG-Solar | X |  |  |  |  |  |  |  |
| McPhee | Peter | MassCEC (alt) | State Agency |  |  |  | X |  |  |  |  |
| Miller | Gary | Unitil | Utility |  | X |  |  |  | X | X | X |
| Moskos | George | NSTAR | Utilities | X | X | X | X |  |  | X | X |
| O’Dougherty | Michael | Spire Solar Systems (alt) | DG-Solar | X |  |  |  |  | X | X |  |
| Pentland | Bill | ClearEdge Power | DG-CHP |  |  | X | X | X | X |  | X |
| Plitch | Larry | Source 1Veolia (alt.) | DG-CHP | X | X | X | X | X |  |  |  |
| Sign in Sheet MA DG Collaborative Working Group Plenaries | 5.31 | 6.13 | 6.28 | 7.12 | 8.1 | 8.23 | 9.5 | 9.6 |
| Roughan | Tim | NGRID | Utilities | X | X | X | X | X | X | X | X |
| Ruiz | Kially | Aquinergy | DG-Wind | X |  |  |  |  |  |  |  |
| Schmidt | Douglas | Harvard | DG-CHP |  | X | X | X |  |  |  |  |
| Smith | Mary | Harvard (alt.) | DG-CHP |  |  |  |  |  |  |  |  |
| Soares | Joe | CLC/CVEC | Cust/Cities | X |  | X | X | X | X | X | X |
| Sprite | Reid | Source One/Veolia Energy | DG-CHP |  | X | X | X | X | X | X | X |
| Stone | Michael | My Generation Energy, Inc. | DG-Solar | X | X | X | X | X | X | X | X |
| Tosches | Jamie | MA AGO | State Agency | X | X |  |  | X | X | X | X |
| Walsh | Kevin | MA AGO | State Agency |  | X | X |  | X | X | X | X |
| Wells | Donald | NU (alt.) | Utilities | X |  |  |  |  |  |  |  |
| Zachas | Rebecca | BCK Law P.C. | Cust/Cities | X | X |  | X | X | X |  | X |
| Other Working Group Participants |
| Sign in Sheet MA DG Collaborative Working Group Plenaries | 5.31 | 6.13 | 6.28 | 7.12 | 8.1 | 8.23 | 9.5 | 9.6 |
| Adamson | Dan | SEIA | DG-Solar |  |  |  |  |  |  | X | X |
| Ahirrao | Vishal | NGRID | Utilities | X |  |  |  |  |  |  |  |
| Argo | Liz | Argo Consulting | Other/Cons | X | X |  |  |  |  |  |  |
| Bachman | Roberto | SolarFlair Energy | DG-Solar | X |  |  |  |  |  |  |  |
| Baker | Ed | UTC Power | DG-CHP | X |  |  |  |  |  |  |  |
| Beck | Don | Keegan Werlin for NSTAR | Other/Law |  |  |  | X |  |  |  |  |
| Bhumgara | Rayo | Sust. Strategies 2050 | DG-Solar | X |  |  | X |  |  |  |  |
| Boecke | Donald | NSTAR | Utilities | X |  |  |  |  |  |  |  |
| Brazo | Shawn | Prime Solutions | DG-Solar |  |  | X |  |  |  |  |  |
| Busch | Joe | Borrego Solar | DG-Solar |  | X |  |  |  |  |  |  |
| Cox | Roger | NGRID | Utilities | X |  |  |  |  |  |  |  |
| DaSilva | John | Aegis Energy Services | DG-CHP | X |  |  |  |  |  |  |  |
| DeVillars | John | BlueWave Capital | DG-Solar | X |  |  |  |  |  |  |  |
| DiNapoli | John | Unitil | Utilities | X |  |  |  |  |  |  |  |
| Dunn | Hayley | ISO-NE | Other |  |  |  | X |  |  |  |  |
| Sign in Sheet MA DG Collaborative Working Group Plenaries | 5.31 | 6.13 | 6.28 | 7.12 | 8.1 | 8.23 | 9.5 | 9.6 |
| Enayati | Babak | NGRID | Utilities | X |  | X |  |  |  |  |  |
| Feraci | Joseph | NSTAR | Utilities |  | X | X | X | X |  | X | X |
| Fitzpatrick | Joseph | DG Clean Power | DG-CHP | X |  |  |  |  |  |  |  |
| Forrest | Dave | ISO-NE | Other |  |  |  | X |  |  |  |  |
| Foster | John | Advanced Energy | DG-Solar | X |  |  |  |  |  |  |  |
| Fox | Kevin | IREC | Other |  |  |  | X |  |  |  |  |
| Fuller | Peter | NRG Energy | DG-Solar | X |  |  |  |  |  |  |  |
| George | Caleb | NGRID | Utilities |  |  |  |  |  | X |  |  |
| Grace | Bob | SEA | Other/Cons |  | X |  |  |  |  |  |  |
| Greenblatt | Beth | Beacon Integrated Solutions | Other/Cons | X |  |  |  |  |  |  |  |
| Greenwood | Daniel | SolarFlair Energy | DG-Solar | X |  |  |  |  |  |  |  |
| Gudell | Jan | NSTAR | Utilities | X |  |  |  |  |  |  |  |
| Habib | Jack | Keegan Werlin for NSTAR | Other/Law |  | X | X |  |  |  | X | X |
| Hawes | Peter | Borrego Solar | DG-Solar | X |  |  |  |  |  |  |  |
| Jones | Keith | NSTAR | Utilities |  | X |  | X |  |  |  |  |
| Keeffe | Andrea | NGRID | Utilities |  | X | X | X |  |  | X | X |
| Kelley | Paul | NSTAR | Utilities | X |  |  |  |  |  |  |  |
| Krathwohl | Eric | Rich May | Other/Law |  |  | X |  |  |  |  |  |
| Krich | Abigail | Boreas Renewables | DG-Wind | X |  |  |  |  |  |  |  |
| Kuriakose | Alex | NGRID | Utilities | X |  |  |  |  |  |  |  |
| LaBrake | Neil | NGRID | Utilities | X | X |  | X | X |  | X | X |
| Larsen | Walker | CLF | Other | X | X | X | X | X | X | X | X |
| Ledgerwood | Bruce | LEAN | Cust/Cities | X |  |  |  |  |  |  |  |
| Medeiros | Ron | NECHPI | DG-Solar | X |  |  |  |  |  |  |  |
| Melnick | Leah | SEA | Other/Cons | X | X |  |  |  |  |  |  |
| Newman | Joe | NGRID | Utilities | X |  |  |  |  |  |  |  |
| Oppenheim | Jerry | LEAN | Cust/Cities |  |  |  |  |  |  | X | X |

| Sign in Sheet MA DG Collaborative Working Group Plenaries | 5.31 | 6.13 | 6.28 | 7.12 | 8.1 | 8.23 | 9.5 | 9.6 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phelps | Nathan | DPU | State Agency | X |  |  |  |  |  |  |  |
| Plett | Frederick | MA AGO | State Agency | X |  |  |  |  |  |  |  |
| Raab | Jonathan | Raab Associates | Other | X | X | X | X | X | X | X | X |
| Rabadjija | Neven | NSTAR | Utilities | X | X |  |  | X | X | X |  |
| Ritter | Jason | Borrego Solar | DG-Solar | X |  |  |  |  |  |  |  |
| Robinson | Camal | NGRID | Utilities |  |  |  |  | X | X |  | X |
| Schroeder | Erica | IREC | Other | X |  | X |  | X | X | X | X |
| Sins | Jack | Unison Energy | DG-CHP | X |  |  |  |  | X |  |  |
| Skulley | Brooke | NGRID | Utilities | X |  |  |  |  |  |  |  |
| Smith | Daniel | Siemens | DG-Solar | X |  |  |  |  |  |  |  |
| Sterritt | Justin | MA EOHED | State Agency | X |  |  |  |  |  |  |  |
| Walker | Jim | Solar PV Grid Tie Ameresco | DG-Solar | X |  |  |  |  |  |  |  |
| Wallerstein | Mike | MA DPU | State Agency | X |  |  |  |  |  |  |  |
| Webster | Raquel | NGRID | Utilities |  |  |  |  |  | X |  |  |
| Wheeler | Lorraine | Redstoke, LLC | Other/Cons | X | X | X |  |  |  |  |  |
| Winter | Danielle | Keegan Werlin for NSTAR | Other/Law |  |  |  |  |  | X |  | X |

# Footnotes

According to the utilities’ presentation at our 2nd Plenary, they have increased DG interconnection-related staff (including contractors) from around ten full-time equivalent in 2008 to 35 full-time equivalent in 2012.