MA DG Collaborative Working Group – Plenary Meeting #5 (8/1/12)

Location: NSTAR, Westwood, MA

Facilitator: Dr. Jonathan Raab, Raab Associates, Ltd.

DRAFT Meeting Summary

Changes made at 8-6  and 8-7 Subcommittee Meetings (at CLF) in Redline

27 people attended the fifth plenary meeting (attendee list can be found in Appendix 2).  Following is a high-level meeting summary as well as updated language for issues the group worked on during the plenary.  The more detailed running meeting notes are available in Appendix 1.  See all the documents from Plenary #5, including the combined meeting summaries/outlined language from the last Process and Technical Subcommittees on the website at: http://massdg.raabassociates.org/events.asp?type=eid&event=63

- Review Goals and Agenda for Day—Jonathan Raab

The group has begun to outline and draft language for consideration at past subcommittee meetings and via homework provided by specific working group participants. For Plenary #5 the group largely worked from these documents while Dr. Raab edited language and outlined points in real-time, discussing and working through relevant issues. No language is yet final, but the group is now developing language that will be the basis for draft recommendations.

- Online Application and Project Tracking System

The group reviewed Centralized Interconnection Application Tracking System (CATS) outline developed for discussion by Gerry Bingham of DOER and also discussed an interim transition strategy to add a “feeder number” field to the current monthly utility reporting. The group discussed the separate but related needs for an online application process and an online project tracking system; both should be seamless (easy to implement), make the application and interconnection process more efficient, and provide clearer information about the status of projects moving through the interconnection process.  The system needs to also communicate easily to and from utility IT systems.

The group has discussed the option of issuing an RFP for a third party system administrator that will centralize and manage the online application and tracking system, syncing it with each of the utilities’ in-house systems.  Below is an outline of the purpose, inputs, outputs, schedule, and overall strategy outlined by the work group during the plenary session.

CATS Proposal Detailed Discussion Notes

- Purpose

  - Centralized Application process

    - Preapplication (report for expedited and standard)

  - Application--Centralized/Standard application process for all 3 tracks (update interconnections applications)

  - Tracking system (transparency)

    - Individual Applications--Utilities and applicants to know where they are in process and deadlines on a particular application through construction (time stamps on steps been thru)

    - Aggregate Applications--To be able to monitor in aggregate timeline compliance (customer & utility) for everyone including regulators

  - Prospecting—Allow developers to see level of activity on specific feeders

- Inputs

  - Customer: Completed application

    - (may require training and minimum knowledge certification)

    - Preapplication Report required information (for expedited and standard)

    - Basic information about application (differs by Track)

    - Automated Application Completeness Check (with checklist)—(

  - Utility

    - Track applicant is in (Standard, Expedited, Simplified)

    - Basic information about application (screens passed, construction timelines/milestones,

    - Communications to customers (where applicant is in process, and time stamps)

    - Point of contact (by stage) at utility and customer

- Outputs

  - Completed preapplication and application back to utility

  - Chess clock (Utility and Applicant)

  - Step where are  in interconnection review process

  - Show Deadlines

  - Ability to sort by feeder (allow developers to sort by feeder to see activity there) and other aggregated sorts

- Schedule (From after DPU Approves Concept)

  - Release (who—MA CEC, DOER, or utilities?) RFP—1 Month

  - Consultant Selected—1 Month

  - DPU Approvial (Is this really needed?)—1 Month

  - Consultant work—3 Months)

    - Design application and tracking processes

    - Design interface strategy with each utility system (both for utility to update central record, and for utilities to get completed application from central system)

    - Design access and security protocols

    - Phasing in strategy

    - On-going cost to run systems

  - DPU Approvial (Is this really needed?)—1 Month

  - Commence Use of System (2-3 Months?)

    - New applications

    - Existing applications (see #5 below)

- Strategy for Dealing w/Projects Already in Queue

  - Use data from monthly reporting spreadsheet for initial population (perhaps do stale project purge first)

  - When utilities next touch application, provide time and step related issue

- Cost Recovery

  - Design and start up thru ACP

  - Ongoing costs by participants

- Questions:

  - Can we use net meter assurance administrator?

  - Costs:

  - On-going costs covered by new application fees, no retroactive assessment

  - Design and start-up costs funded by ACP

  - Other

  - Training

  - What’s public info., and what’s only accessible to applicant/utility.

Update to Transition Strategy for Adding Feeder Info to Monthly Utility Report

The plenary updated the list of potential priorities and potential sequencing for populating the spreadsheet as described below.  It also discussed whether to use just the feeder number, or also include specific location information, and agreed to focus on just the feeder number for the monthly spreadsheet.  The utilities offered to provide the feeder information in its next monthly report (August), and other information in (October):

- All new complete applications (all tracks)—once utility knows the correct feeder, the number will appear in the report approximately 1 Month after— Starting with the August 2012  report

- All existing projects utilities touch—Starting August 2012 report

- All projects (in process or with authorization to interconnect) over 1 MW—for October 2012 report

(Note: No Timelines yet for the following (which could become moot once centralized tracking system is up and working.)

- All projects with authorization to interconnect (Expedited/Standard)  (October ??)

- All Standard projects

- All Expedited projects

- All Simplified Projects (not reported in monthly reporting at all now)

The work group also notes that NSTAR has voluntarily added two other columns to their monthly reporting: 1) Municipal, C/I, residential designation; and 2) Date they asked applicant for additional info.  The group agreed that the new feeder number field should be three columns from the end of the existing report, so allow DOER to easily integrate the spreadsheets from all utilities.

- Adding a Required Pre-Application Report and Optional Feasibility Study Steps (for Expedited/Standard only)

The point of both a required pre-application report and optional feasibility study are to improve the process by “screening” potential projects early  (i.e. spend a little more time upfront to decrease number of applicants/improve quality of applicants and thereby shorten the time projects spend in the application process).

Pre-application Report

The work group agreed to the following outline for a required pre-application report that the utility would provide applicants to the expedited and standard processes.  There was ongoing discussion around how to define the “nearest” feeder, although the working group has suggested that the report will provide the feeder number rather than a location. Potential applicants will be able to make informed decisions by using the feeder number provided in the report and the feeder number data that will now be provided in the monthly utility reports. Whether or not to provide the distance to the nearest substation and whether to provide a google snapshot of the areas is still being discussed. The utilities suggest that the actual substation, and feeder, may change as the project progresses, so there is little reason to provide information about which substation is closest to the project location. Factors other than distance may impact which substation is used. Developers suggest adding language that explains this, so potential applicants understand the information about nearest facilities is legally qualified. There would be no direct charge for the pre-application report, but the cost would be absorbed through the general application fees.  The work group did not yet set a timeframe for the pre-application report.

SEE NOTES BELOW FEASABILITY STUDY TO SEE NEW PREAPPLICATION  RECOMMENDATION FROM SUBCOMMITTEE FOR REPORT

# Pre-Application Process

## General Information

A Pre-Application will be required for all (Expedited and Standard but not simplified) proposed projects.

There will be no costs to the developer for a Pre-Application.

All information provided by the utility is non-binding and considered to be for reference purposes only.

## Required Information from Applicant:

Contact information

Proposed location (address and nearby cross street and Google map)

Type of DG (solar, wind, CHP)

AC  KW Size(s)

Exporting or non-exporting (Is it stand alone?)

New electric service or existing service (Is it behind existing service—if so customer account #, minimum/maximum load)

## Information provided by utility:

- Feeder/circuit voltage

Voltage at proposed location

Single or three-phase

If single-phase, how far away is three-phase?

How much DG on circuit (connected and proposed)

Radial, area network, or spot network

Nearest (2) Feeders (within 2 miles) number/designation

Distance to sub-station???

Snap shot (quarter mile)

Utility Can Provide Additional Comments

Feasibility Study

Reid Sprite presented an outline of a potential feasibility study concept (see Appendix 3. The FS concept is to use the same information potential applicants submit for the pre-application report, but allow them to pay a fee to request an optional FS from the utility that would provide more detailed information than the pre-application report before the project formally applies. After some discussion among the work group, it was felt that the proposal was tantamount to a mini-Impact Study, and might be too complicated to add into the existing process.  However, the work group agreed to continue to explore the concept of a less ambitious “initial review” option perhaps with a bit more information provided by the applicant in a “streamlined application.”  During this discussion the work group also flagged the issue of needing a better way to handle applications that substantially change during the review process mid-stream.

The Technical Subcommittee is recommending combining the required pre-application report and feasibility study into a required pre-application basic report or a more detailed report, as outlined below.  Text highlighted in yellow is still under discussion.

Applicant provides the following information which would be the same for the basic report or the more detailed report:

- Project Contact Information

Name:

Address:

Phone:

Email:

- Location (street address with nearby cross streets, town):

- Generation Type: (solar, wind, CHP)

- Size (AC kWs):

- Single or three phase generator  configuration:

- Stand-alone (no on-site load – Y or N):

- If Existing service (include customer account number, site minimum and maximum (if available) current or proposed electric loads in kWs)?

- New service needed?

Utility basic report includes Items 1-7,  utility includes Items 1-14 for more detailed report)

- Circuit voltage:

- Circuit name:

- Voltage at proposed location:

- Single or three phase available near site:

- If single phase – distance from three phase service:

- Aggregate connected and submitted applications of DG on circuit:

- Area network, or spot network or radial:

- Distance from nearest sub-station

- If nearest feeder is ‘full of DG’, closest available feeder with capacity

- Determination of likely project track

- Peak load on proposed feeder

- Electrical dependence on other proposed projects

- Other potential constraints or critical items that may jeopardize project

- Potential infrastructure upgrade information (see below)

- Snap-shot within ¼ mile??

- Whether their application will likely trigger (or require to be part of) cluster study

Basic Report Time: 10 business days

More Detailed Report Time: 20 business days

Basic Report Fee: Free

More Detailed Report Fee: $750--$1,000

Required vs. Optional: One or the other is required for expedited and standard tracks only

Monthly quota: no more than 5 Reports/month or should there be small fee for basic Report?

Disclaimer: Be aware that this is simply a snapshot in time and is non-binding, system conditions can and do change frequently. (Note; Impact studies generally run around $10,000 per MW).

Add to list of things to work on post-Sept over next year?—accessible geographic mapping that will show feeders/circuits and DG activity (including names of sub-stations, circuits served)

- Multiple Projects on a Single Feeder (Cluster Studies)

The utilities stated that they are learning from the voluntary clustering projects currently underway, but that they don’t have enough experience to feel comfortable hard-wiring a mandatory clustering requirement at this time.  The work group agreed that while it might be premature to mandate cluster studies that utilities should be required to offer a formalized clustering option to applicants when there are multiple applications on a single feeder that are electrically dependent.  It would then be up to the applicants to agree to go forward with a cluster approach or not.  The work group further agreed that it should establish study and upgrade cost allocation guidelines now, and is generally comfortable with the following proposal:

- Study Cost Allocation—by MW

- Upgrade Cost Allocation

  - Lines—Share common segments pro rata by MW, unique segments covered by that DG provider

  - Other equipment—Share common upgrades pro rata by MW, unique upgrades by that DG provider

  - If one or more DG applicant drops out, then remaining applicant share any additional restudies required

  - If new DG added to circuit within 5 years, need to share costs from prior DG (consistent w/utility line extension policy) (some exemptions—e.g., Simplified?)

The work group discussed, but did not resolve, how much time a cluster study should take.  The work group agreed to have the subcommittees flesh out a formalized but optional clustering approach.

Formalized Required Group Study Proposal (NOTE: Subcommittee recommending that this be required and not optional in contrast to last Plenary discussion.)

- Exhausted (or near-exhausted) Feeders and/or Where New Express Feeder is Needed)

  - Utility decides when application triggers exhausted feeder, and that opens up group study window

  - Group study process is required

  - Open enrollment window for 3 months

  - Should open cluster be advertised??

  - 75 days for impact study/75 days for detailed study

  - Follow cost allocation of study and upgrade costs oulined (above)

  - Other Group Study Options

  - Optional in other circumstances if applicants come together and propose to utility

- Other Comments from Technical Subcommittee

- If can release name/contact info.  in blanket fashion or have customers check off box to release, would facilitate applicants finding each other for #2 above

- Need criteria to help guide utilities where else to potentially offer optional clustering

- Once cluster initiated, utility should follow same guidelines for cost allocation etc.

  - Should this be voluntary, or required (like CA)?

  - Should it also be retroactive to help move things along after the initial “purge”?

- Screens, Timelines, and Fee Issues

- Simplifed Track Screen

The work group agreed to change one of the existing screens (Is the aggregate generating Facility capacity on the circuit less than 7.5% of circuit annual peak load?) to potentially allow more DG thru the simplified by track, as follows: Is the aggregate generating Facility capacity 15% of feeder/circuit and, if available, line segment?

- Simplified Spot Network Track Screens

Utilities are studying area networks to develop the data needed to come up with appropriate/safe screens for area networks. The DG reps made clear they consider area networks an important issue and expect the work group to address interconnection to area networks.

The work group discussed at length the subcommittee’s recommendation to allow the simplified spot network screens to also apply to area networks, and ultimately agreed to allow the Simplified option on both spot and area networks (if other screens are passed) as long as applicant has interval meter data for an appropriate time period, and where available minimum load data, for area networks. The work group also agree to accept the subcommittees recommendation to remove the requirement that the system be less than or equal to 15 kw, as long as less than 1/15 of Customer’s minimum load is met.  The work group also agreed to

develop language for the Report about continuing to monitor and track IEEE 1547 and national best practices and to study and experiment in Massachusetts on area networks (e.g., NSTAR pilot project).  They also agreed to incorporate networks and IEEE handling of networks into utility standardized guidelines (e.g., National Grid (ESB 756-C) guidelines/standards.

- Construction Timelines

The group also continued to discuss the need for stricter, more formalized construction timelines (with clear milestones).  The work group discussed the fact that the utility can’t provide a clear construction schedule at the time of the interconnection agreement if the applicant waives the detailed study, as the utility essentially still needs to do the detailed study before they can figure out the construction schedule.  DG construction schedules also currently must dovetail with all other utility construction projects—they do not have unique priority.  Group agreed that there should be clear timelines w/milestones that should be tracked like the steps in the interconnection agreement steps.  At the same time, there’s recognition that there are many reasons that construction schedules slip on both the DG and utility side and needs to be clearly laid out contingencies.

- Construction schedules/milestones need to be in the Interconnection Agreement (i.e., at end of Detailed Study,  or if take +/- 25% option have ranged construction schedule after Impact Study and then final construction schedule usually after utility does its own Detailed Study (utility design engineering).  Consider changing “Detailed Study” to “Utility Design Engineering Process”.

- Should there be standard, default utility construction schedule (e.g., 30-60 days) and just by mutual agreement for large, complex projects?

- Construction schedules need to be adhered to on both sides unless clear cause (see net metering document for definition of cause)

- Add reference in Section 5

- Construction schedules should be tracked.

- Should there be clear enforcement mechanism (incentives/disincentives)?

- Dealing With Large Projects

The group discussed potential screens for large projects that are currently taking more time to study. The suggested screens include projects that are stand alone (i.e., are new services primarily for export of power with little or no native load) and are over 1MW. If a project meets these screens, the utilities propose a longer timeline due to increased study complexity (e.g., 75 days instead of 30 for the detailed study and possibly more time for the impact study). The work group asked the utilities to formalize their proposal in writing, and asked IREC to provide information on how other states are handling similar large projects.

Utility Proposal: 4th track or modification of the Standard process

What is covered:

Any generator exporting 1MW or larger at any time, or any proposed generation where the proposed generation and the aggregated DG on the feeder is larger than the minimum load on the feeder.

Impact study issues:

Generators larger than 1 MW or where the aggregated DG is larger than the minimum load requires additional work than in a standard impact study. The additional work can include:

- anti-islanding study

- ground fault detection study

- additional studies required for ISO-NE review and approval

  - Attachment 4 submittal for projects greater than 1 MW but less than 5 MW

  - Transmission Stability Analysis, TTF, and STF review and approval for projects 5 MW and greater

  - Compliance with utility UFLS, underfrequency generator trip requirements

- Evaluation of impacts on substation LTC’s, feeder regulators, and switched capacitor banks

- Evaluation of alternative upgrade packages to resolve identified problems

- System Upgrade Evaluation

  - Reconfiguration of distribution  feeders to resolve or eliminate mutual impacts among applicants

  - Circuit conductor upgrades

  - Evaluation of fault current contribution mitigation

  - Dedicated feeders to be constructed to connect large DG applicants

  - Evaluation of nonconventional solutions, such as DVAR/STATCOM or battery backup system

- Cost Estimating and Project Coordination

- Multi-MW interconnection projects involve evaluation and production of cost estimates that involve and cut across multiple disciplines at a utility company.   System Planning, Metering, Distribution Engineering, Transmission Engineering, Maintenance & Construction, Control & Protection, Right-of-Way, etc.   The larger a proposed project is, the more departments need to be involved, and the longer the time frame needed to comply with a System Impact Study Report and a Detailed Facilities Study

If the studies in 1 or 2 above show that either of these will need to be resolved, it involves either direct transfer trip (DTT) on the feeder breaker at the substation or the installation of ground fault detection on the high side (transmission voltage – 69 kV or higher) of the substation transformer.

Solution:

Provide 75 business days to complete the impact study

Detailed facilities study issues:

If the impact study shows that substation work will be required (as outlined above), significantly more work is required to properly estimate the costs and construction schedule for this increased level of work. DTT requires looking at up to 5 communication options (landline, wifi, radio, powerline carrier, fiber) and modifying the feeder breaker to accept the control scheme to determine the most cost-effective and timely solution. Ground fault relay detection requires installation of potential transformers (if there are  existing ones, they can’t be over-burdened) and the necessary relaying and protection devices to be installed. Any print (wiring and relay diagrams) of the substation that is affected (and there can be 100 or more prints per substation) need to be reviewed to make sure there is no inadvertent interaction, and re-drawn to show the new as-built for future trouble-shooting of the relaying at the substation.

Solution:

Provide 75 business days to complete the detailed facilities study

DG Proposal on Adjusting Expedited Screens to potentially allow more currently going thru Standard process to Expedited

Add CA Screens N, O, and P to supplemental review—if pass these still eligible for Expedited:

N:    penetration test—power flows from circuit back to sub will have minimum impact

O:   power quality and voltage test--…

P:  safety and reliability test—can adequately be addressed w/o impact study

Need to also clarify what’s happening in the 20 day supplemental review phase.

Additional Thoughts from Group and Next Steps

Consider lifting 10 hour limitation on Supplemental Review in Expedited to allow more to stay in Expedited.

Review existing MA Expedited screens (seam between Expedited and Standard), and consider CA screens

More crisply define the Standard vs. 4th track delineation—when will it kick in (e.g., big line extension needed or sub-station modifications)?

Should new standards apply to only new applications, or also pre-existing ones?

Review timelines for Expedited and Standard overall timelines, and timelines for each step.

Handling renegotiation?

- O&M Costs

O&M cost issues were not discussed due to time constraints

- Adherence to Timelines Strategies

- Customer Timelines: Stale Project Management

The group discussed timeline adherence strategies from both the customer and utility side. Stale projects occur when customers do not meet their timelines for providing information or other required documents, and appear to be inactive. Although this is most problematic on feeders where they are holding up other projects queued behind them, it is also an issue on feeders without a queue (utilities need to periodically ping them, and it fans the perception that there are lots of active projects not being interconnected.  The group discussed strategies for both an initial purge of inactive projects, as well as an on-going approach to dealing with stale projects.  For the initial purge, the work group was clear that applicants should have adequate notice before being purged (e.g., perhaps two notices and 30 days to re-activate their application by complying with the original data or document request).   Regarding an on-going process, continued to discuss whether to apply purge rules to all projects regardless of whether or not they are holding up any other projects, or only those with a queue behind them. The mechanism under consideration is a non-discretionary process that customers are clearly informed about their deadlines for data or document compliance, informed when a deadline is missed and given a reasonable opportunity to cure, and are then removed if they don’t cure.  There may be some limited exceptions, and then there’s the ADR process.

- Initial Withdrawal

  - For all applicants where utility waiting to hear from the customer at any level at any stage (in application and construction process) for more than 30 business days

  - Utility contacts applicant (email  and letter and/or phone if no email address)—customer of record, alternative contact, and a most recent point of contact

  - Haven’t heard from you in over 30 business days, if don’t hear from you in 30 business days, we will consider your application withdrawn (and if you want to continue at a later date, you will need to reapply).  Any fees not refunded.

  - (Indicate removal being required by DPU)

- On-Going Customer Timeline Compliance (for all projects whether on queue or not)

  - Notice (email  and letter and/or phone if no email address) that deadline elapsed, and given one extension before considered withdrawn

  - Extend initial deadlines at each stage equal to deadline  ( w/o cause)

  - Allow additional extensions with cause (possibly as per net metering assurance language)

  - Would need to base metrics on utilities side of chess clock only

  - Projects then considered withdrawn and need to reapply

- Timeline (after DPU approval)

  - Initial Withdrawal—Begin right after DPU approval (2-3 months to complete)

  - On-Going Customer Timeline Compliance—Concurrently w/Initial withdrawl or after/sequential?

- Utility Timelines: Timeline Assurance/Enforcement

With regard to an assurance strategy (utility side), the group discussed broadly how there can be greater assurance that timelines are met in an enforceable manner.  The utilities discussed the steps they are all taking to improve internal processes and procedures and marshal adequate resources to work on interconnecting DG. They also reiterated their reluctance to negotiate “penalties”. The group reviewed Section 49 of SB 2395 (below), and discussed, without reaching any conclusion how, if at all, the Legislation should and will impact the work group negotiations on assurances.

The department of public utilities shall develop an enforceable standard interconnection timeline for the interconnection of distributed generation facilities. Timelines may vary depending on the size and type of the facility or other factors as determined by the department. The department shall implement such timeline not later than November 1, 2013. The department shall enforce established timelines as part of its service quality standards review under section 1I of chapter 164 or by whatever enforcement mechanism is determined

appropriate by the department.

Discussion;

- Principles for consideration:

  - Let utilities also be allowed to have timelines slip in certain clear circumstances for good cause

- Focus on enforcement mechanisms first that have both incentives/offsets and disincentives, rather than just disincentives

- Reid—Went over Service Quality example, discussed:

  - Doesn’t include projects still in queue in Reid’s analysis

  - Should this be part of existing service quality metrics, or stand alone service quality metric?

  - Existing service quality metric designed more for all ratepayers than narrow groups of customers

- DOER has another enforcement construct and plans to release for discussion before the Plenary session

AG Presentation on Cost and Cost Allocation

(See presentation on DG website under 8/6)

- O&M already mentioned in the tariff (but not collected according to utilities)

- Should system benefits be credited to DG provider—how account for it?

- Get avg cost for processing DG applications (simplified, expedited, standard) separate from the impact/detailed study costs?

- What are circumstances that have led to cost-sharing?

- O&M costs that aren’t being recovered?

- Should the tracking system track the costs (system and customer costs for interconnection)?

UTILITIES WILL COME TO NEXT PLENARY w/INFO OR GAMEPLAN FOR ALL ABOVE

- Upgrade Criteria and Standards (e.g., National Grid’s “Blue Book”) (from 7/19 Technical Subcommittee and amended on 8/7)

The technical Subcommittee discussed National Grid’s upgrade criteria and standards manual, and were generally very supportive of the document, with the following recommendations:

  - Add information on  infrastructure/system modifications upgrade criteria

  - Update regularly (e.g., 2-5 years), w/DG provider input

  - Goal one statewide document, even if has to be some differences within that document among the utilities (for starters utilities reviewing NGRID document against their own guidelines and will highlight any substantive differences w/NGRID standards)

  - Meet regularly to discuss with stakeholders new technology, criteria and standards (e.g., monthly or quarterly)

  - For Sept. will have process laid out including schedule (identify any differences w/Grid; utility drafts; etc.)

To Do List From 8/7-8 Subcommittees

- Post subcommittees meeting summary—Raab

- Post agenda for Plenary #6—Raab

- Develop and circulate draft Report Outline (est 8/21)—Raab

- 3rd Monthly report to DPU by 8/11—Raab

- Documented costs for current application process and O&M—Utilities

- Detailed proposal on revised timelines and screens for Expedited, Standard, and Potential new 4th track—Utilities

- Assurance/Enforcement of Timelines—Everyone

Review Revised Recommendations from Subcommittees on All Issues (shown in redline) and pay special attention to and attend to any implicit TO DO’s language still under discussion (yellow highlights) throughout this document--ALL

Appendix 3 Feasibility Study Outline

Feasibility Study Recommendations

# Feasibility Study

## General Information

Generally, the Feasibility Study would be performed by the utility at the developer’s discretion and would not be required for projects that export 5 MW or less.  For projects exporting more than 5 MW, the Feasibility Study would be required.

The Feasibility Study shall be performed prior to the submission of a full application.

The information required by the utility should be the same as the info that is required for a Pre-Application.

The Feasibility Application should be considered as a simple “up-charge” from the current Screening Memos that are provided by some utilities.

All information and estimates provided by the utility are non-binding and considered to be for reference purposes only.

## Fees

A study fee would be incurred by applicants that opt to have a Feasibility Study performed.

Non-exporting facilities:  $250

Projects exporting 1 MW or less:  $1,000

Projects exporting 1 MW to 5 MW:  $2,500

Projects exporting over 5 MW:  $4,000

## Required Information from Applicant:

- Contact information

Proposed location (address and Google map)

Type of DG (solar, wind, CHP)

Size(s)

Exporting on non-exporting

New electric service or existing service

## Information provided by utility:

- Compliance review of existing screens and determination of appropriate project track

Peak load on proposed feeder

Size and type of DG on feeder (connected and proposed)

Electrical dependence on other proposed projects

Rated feeder capacity and peak load

Major distribution line equipment upstream from proposed feeder location

Reclosers

Capacitor banks

Voltage regulators

Step-down transformers

Description of substation

Number and size of station transformers

LTC/regulator capabilities

Bus arrangement

Potential infrastructure upgrade information

High-level estimate of distribution and substation upgrades (+/- 50%)

Available capacity before major infrastructure upgrades are required

Estimated timeline for construction of infrastructure upgrades

Limiting factors of current infrastructure

Other potential constraints or critical items that may jeopardize project

# Timelines

It is intended that the Study will be performed within the timelines in the current tariff allowed for “Complete Review of All Screens” and “Complete Standard Process Initial Review”.  As such, the Study shall be completed within 25 working days for the both the Expedited and Standard tracks.  Refer to the attached tables for a detailed list of proposed timelines.

Expedited Track Timeline

| Current Expedited Process |  | Proposed Expedited Process |
| --- | --- | --- |
|  |  |  | Pre-Application timeline | w/out Feasibility Study | w/ Feasibility Study |
|  |  |  | Utility provides Pre-Application response | 5 days | 5 days |
|  |  |  | Optional: Developer requests Feasibility Study |  |  |
|  |  |  | Utility sends Feasibility Study cost and agreement |  | 3 days |
|  |  |  | Developer submits payment and returns agreement |  | 3 days |
|  |  |  | Complete review of all screens / Complete Feasibility Study | 20 days | 25 days |
| Application timeline |  |  | full application timeline |  |  |
| Acknowledge Receipt of Application | 3 days |  | Acknowledge Receipt of Application | 3 days | 3 days |
| Review Application for Completeness | 10 days |  | Review Application for Completeness | 10 days | 7 days |
| Complete Review of All Screens | 25 days |  |  |  |  |
| Send executable agreement | 10 days |  | Send executable agreement | 10 days | 10 days |
| Total maximum days | 48 days |  | Total maximum days | 48 days | 56 days |

Standard Track Timeline

| Current Standard Process |  | Proposed standard Process |
| --- | --- | --- |
|  |  |  | Pre-Application timeline | w/out Feasibility Study | w/ Feasibility Study |
|  |  |  | Utility provides Pre-Application response | 5 days | 5 days |
|  |  |  | Optional: Developer requests Feasibility Study |  |  |
|  |  |  | Utility sends Feasibility Study cost and agreement |  | 3 days |
|  |  |  | Developer submits payment and returns agreement |  | 3 days |
|  |  |  | Complete review of all screens / Complete Feasibility Study | 20 days | 25 days |
| Application timeline |  |  | full application timeline |  |  |
| Acknowledge Receipt of Application | 3 days |  | Acknowledge Receipt of Application | 3 days | 3 days |
| Review Application for Completeness | 10 days |  | Review Application for Completeness | 10 days | 7 days |
| Complete Initial Review | 20 days |  |  |  |  |
| Send Follow-on Studies Cost/Agreement | 5 days |  | Send Follow-on Studies Cost/Agreement | 5 days | 5 days |
| Complete Impact Study | 55 days |  | Complete Impact Study | 50 days | 50 days |
| -Completed Detailed Study | 30 days |  | Completed Detailed Study | 30 days | 30 days |
| Send executable agreement | 15 days |  | Send executable agreement | 15 days | 15 days |
| Total maximum days | 138 days |  | Total maximum days | 138 days | 146 days |